## Input
Range
Projectname | ENDK
PSCAD Namespace | ENDK
Pn | 100 | MW
Uc | 161.9 | kV
Un | 152 | kV
Area | DK1
SCR min | 3 | -
SCR tuning | 13.5637 | -
SCR max | 14.3859 | -
X/R SCR min | 12.1893 | -
X/R SCR tuning | 12.1893 | -
X/R SCR max | 12.1152 | -
R0 | 0 | ohm
X0 | 1 | ohm
Default Q mode | Q | -
PSCAD Timestep | 2 | µs
PSCAD Volley | 8 | -
Initialization time | 3 | s
U> | 1.1 | p.u.
U> time | 60 | s
U>> | 1.15 | p.u.
U>> time | 0.2 | s
U>>> | 1.2 | p.u.
U>>> time | 0.1 | s
U< | 0.9 | p.u.
U< time | 60 | s
f> | 51.5 | Hz
f> time | 0.2 | s
f< | 47.5 | Hz
f< time | 0.2 | s
df/dt pos | 2.5 | Hz/s
df/dt pos time | 0.08 | s
df/dt neg | -2.5 | Hz/s
df/dt neg time | 0.08 | s

## Area values
| DK1 |  |  | DK2
Un | <110 kV | 110 kV <= Un < 300 kV | 300 kV <= Un | <110 kV | 110 kV <= Un < 300 kV | 300 kV <= Un | Selected
Power-frequency control
LFSM-O start (Hz) | 50.2 | 50.2 | 50.2 | 50.5 | 50.5 | 50.5 | 50.2
LFSM-O droop (%) | 5 | 5 | 5 | 4 | 4 | 4 | 5
LFSM-U start (Hz) | 49.8 | 49.8 | 49.8 | 49.5 | 49.5 | 49.5 | 49.8
LFSM-U droop (%) | 5 | 5 | 5 | 4 | 4 | 4 | 5
FSM deadband (Hz) | 0 | 0 | 0 | 0 | 0 | 0 | 0
FSM droop (%) | 6 | 6 | 6 | 6 | 6 | 6 | 6
FSM provision (%Pn) | 10 | 10 | 10 | 10 | 10 | 10 | 10
30min operation Fmax | 51.5 | 51.5 | 51.5 | 51.5 | 51.5 | 51.5 | 51.5
30min operation Fmin | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5
Reactive power capability (base Uc)
UQ Q=0pu Umax | 1.05 | 1.118 | 1.05 | 1.05 | 1.05 | 1.05 | 1.118
UQ Q=0pu Umin | 0.9 | 0.968 | 0.9 | 0.9 | 0.9 | 0.9 | 0.968
UQ Q=+0.33pu Umax | 1.04 | 1.108 | 1.04 | 1.04 | 1.04 | 1.04 | 1.108
UQ Q=+0.33pu Umin | 0.9 | 0.968 | 0.9 | 0.9 | 0.9 | 0.9 | 0.968
UQ Q=-0.33pu Umax | 1.05 | 1.118 | 1.05 | 1.05 | 1.05 | 1.05 | 1.118
UQ Q=-0.33pu Umin | 0.96 | 1.028 | 0.96 | 0.96 | 0.96 | 0.96 | 1.028
Cont. operation Umax | 1.1 | 1.118 | 1.05 | 1.1 | 1.05 | 1.05 | 1.118
Cont. operation Umin | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
60min operation Umax | 1.1 | 1.15 | 1.1 | 1.1 | 1.1 | 1.1 | 1.15
60min operation Umin | 0.9 | 0.85 | 0.85 | 0.9 | 0.9 | 0.9 | 0.85
LVFRT
LVFT start | 0.9 | 0.85 | 0.85 | 0.9 | 0.9 | 0.9 | 0.85
LVFRT stop | 0.9 | 0.85 | 0.85 | 0.9 | 0.9 | 0.9 | 0.85
Ures | 0.15 | 0 | 0 | 0.15 | 0 | 0 | 0
tclear | 0.25 | 0.15 | 0.15 | 0.25 | 0.15 | 0.15 | 0.15
Uclear | 0.15 | 0 | 0 | 0.15 | 0 | 0 | 0
trec1 | 0.25 | 0.15 | 0.15 | 0.25 | 0.15 | 0.15 | 0.15
Urec1 | 0.15 | 0 | 0 | 0.15 | 0 | 0 | 0
trec2 | 0.25 | 0.15 | 0.15 | 0.25 | 0.15 | 0.15 | 0.15
Urec2 | 0.9 | 0.85 | 0.85 | 0.9 | 0.9 | 0.9 | 0.85
trec3 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
OVRT
U1 | 1.2 | 1.3 | 1.3 | 1.2 | 1.3 | 1.3 | 1.3
t1 | 5 | 0.1 | 0.1 | 5 | 0.1 | 0.1 | 0.1
U2 | 1.15 | 1.2 | 1.2 | 1.15 | 1.2 | 1.2 | 1.2
t2 | 60 | 30 | 30 | 60 | 30 | 30 | 30

## Cases
[18 empty] | Event 1 |  |  |  | Event 2 |  |  |  | Event 3 |  |  |  | Event 4 |  |  |  | Event 5 |  |  |  | Event 6 |  |  |  | Event 7 |  |  |  | Event 8 |  |  |  | Event 9 |  |  |  | Event 10 |  |  |  | Event 11 |  |  |  | Event 12
Rank/Id | RMS | EMT | Name | U0 | P0 | FSM | Qmode | Qref0 | SCR0 | XR0 | Simulationtime | Pref recording | Qref recording | Voltage recording | Inst. Voltage recording (EMT ONLY) | Phase recording | Freq. recording | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2
1 | TRUE | TRUE | SS_Q1 | 1.0651 | 0 | FALSE | Q | 0 | 3 | 12.1893 | 60
2 | TRUE | TRUE | SS_Q2 | 1.0651 | 0.5 | FALSE | Q | 0.2 | 3 | 12.1893 | 60
3 | TRUE | TRUE | SS_Q3 | 1.0651 | 0.5 | FALSE | Q | -0.2 | 3 | 12.1893 | 60
4 | TRUE | TRUE | SS_Q4 | 1.0651 | 1 | FALSE | Q | 0.33 | 3 | 12.1893 | 60
5 | TRUE | TRUE | SS_Q5 | 1.0651 | 1 | FALSE | Q | -0.3 | 3 | 12.1893 | 60
6 | TRUE | TRUE | SS_Uctrl1 | 0.968 | 0.7 | FALSE | Q(U) | 1 | -1 | 0 | 60
7 | TRUE | TRUE | SS_Uctrl2 | 1.118 | 0.7 | FALSE | Q(U) | 1 | -1 | 0 | 60
8 | TRUE | TRUE | SS_PFctrl | 1.0651 | 0.7 | FALSE | PF | 0.949 | 3 | 12.1893 | 60
9 | TRUE | FALSE | P_step_up_0.0_0.5 | 1.0651 | 0 | FALSE | Default | 0 | 3 | 12.1893 | 155 | [6 empty] | Pctrl ref. | 0 | 0.5 | 0
10 | TRUE | TRUE | P_step_up_0.5_0.7 | 1.0651 | 0.5 | FALSE | Default | 0 | 3 | 12.1893 | 65 | [6 empty] | Pctrl ref. | 0 | 0.7 | 0
11 | TRUE | FALSE | P_step_up_0.7_1.0 | 1.0651 | 0.7 | FALSE | Default | 0 | 3 | 12.1893 | 95 | [6 empty] | Pctrl ref. | 0 | 1 | 0
12 | TRUE | FALSE | P_step_down_1.0_0.7 | 1.0651 | 1 | FALSE | Default | 0 | 3 | 12.1893 | 95 | [6 empty] | Pctrl ref. | 0 | 0.7 | 0
13 | TRUE | FALSE | P_step_down_0.7_0.5 | 1.0651 | 0.7 | FALSE | Default | 0 | 3 | 12.1893 | 65 | [6 empty] | Pctrl ref. | 0 | 0.5 | 0
14 | TRUE | FALSE | P_step_down_0.5_0.0 | 1.0651 | 0.5 | FALSE | Default | 0 | 3 | 12.1893 | 155 | [6 empty] | Pctrl ref. | 0 | 0 | 0
15 | TRUE | TRUE | FSM_step | 1.0651 | 0.7 | TRUE | Default | 0 | 3 | 12.1893 | 48 | [6 empty] | Frequency | 0 | 50.199 |  | Frequency | 8 | 50 |  | Frequency | 16 | 49.801 |  | Frequency | 24 | 50 |  | Frequency | 32 | 50.15 |  | Frequency | 40 | 49.85
16 | TRUE | TRUE | FSM_LFSMO_ramp | 1.0651 | 0.5 | TRUE | Default | 0 | 3 | 12.1893 | 40 | [6 empty] | Frequency | 0 |  | 0.0725 |  | 30 | 50
17 | TRUE | TRUE | FSM_LFSMU_ramp | 1.0651 | 0.5 | TRUE | Default | 0 | 3 | 12.1893 | 40 | [6 empty] | Frequency | 0 |  | -0.0725 |  | 30 | 50
18 | TRUE | TRUE | FSM_rec_pstep | 1.0651 | 0.7 | TRUE | Default | 0 | 3 | 12.1893 | [6 empty] | caseInputFiles/DK1_frekvens.meas | Pctrl ref. | 1 | 0 | 0
19 | TRUE | TRUE | LFSM-OU_step | 1.0651 | 0.5 | FALSE | Default | 0 | 3 | 12.1893 | 60 | [6 empty] | Frequency | 0 | 50.45 |  | Frequency | 8 | 50 |  | Frequency | 16 | 49.55 |  | Frequency | 24 | 50 |  | Frequency | 32 | 51.05 |  | Frequency | 46 | 51.45
20 | TRUE | TRUE | LFSMO_ramp+pstep | 1.0651 | 0.5 | FALSE | Default | 0 | 3 | 12.1893 | 40 | [6 empty] | Frequency | 0 |  | 0.075 | Frequency | 20 |  | 0 | Pctrl ref. | 2 | 1
21 | TRUE | TRUE | LFSMU_ramp | 1.0651 | 0.5 | FALSE | Default | 0 | 3 | 12.1893 | 40 | [6 empty] | Frequency | 0 |  | -0.125 | Frequency | 20 |  | 0
22 | TRUE | TRUE | U-Q/Pn_N_up | 1.0651 | 1 | FALSE | Q | 0 | -1 | 0 | 50 | [6 empty] | Voltage | 0 | 1.118 |  | Frequency | 40 | 1
23 | TRUE | TRUE | U-Q/Pn_N_down | 1.0651 | 1 | FALSE | Q | 0 | -1 | 0 | 50 | [6 empty] | Voltage | 0 | 0.968 |  | Frequency | 40 | 1
24 | TRUE | TRUE | U-Q/Pn_UE_up | 1.0651 | 1 | FALSE | Q | -0.33 | -1 | 0 | 50 | [6 empty] | Voltage | 0 | 1.118 |  | Frequency | 40 | 1
25 | TRUE | TRUE | U-Q/Pn_UE_down | 1.0651 | 1 | FALSE | Q | -0.33 | -1 | 0 | 50 | [6 empty] | Voltage | 0 | 1.028 |  | Frequency | 40 | 1
26 | TRUE | TRUE | U-Q/Pn_OE_up | 1.0651 | 1 | FALSE | Q | 0.33 | -1 | 0 | 50 | [6 empty] | Voltage | 0 | 1.108 |  | Frequency | 40 | 1
27 | TRUE | TRUE | U-Q/Pn_OE_down | 1.0651 | 1 | FALSE | Q | 0.33 | -1 | 0 | 50 | [6 empty] | Voltage | 0 | 0.968 |  | Frequency | 40 | 1
28 | TRUE | TRUE | Q(u)_up_1 | 1.0651 | 1 | FALSE | Q(U) | 1 | -1 | 0 | 30 | [6 empty] | Voltage | 0 | 1.118
29 | TRUE | FALSE | Q(u)_up_2 | 1.118 | 1 | FALSE | Q(U) | 1 | -1 | 0 | 30 | [6 empty] | Voltage | 0 | 1.118
30 | TRUE | TRUE | Q(u)_up_3 | 1.118 | 1 | FALSE | Q(U) | 1 | -1 | 0 | 30 | [6 empty] | Voltage | 0 | 1.15
31 | TRUE | TRUE | Q(u)_down_1 | 1.0651 | 1 | FALSE | Q(U) | 1 | -1 | 0 | 30 | [6 empty] | Voltage | 0 | 0.968
32 | TRUE | TRUE | Q(u)_down_2 | 0.968 | 1 | FALSE | Q(U) | 1 | -1 | 0 | 30 | [6 empty] | Voltage | 0 | 0.9
33 | TRUE | TRUE | Q(u)_down_3 | 0.9 | 1 | FALSE | Q(U) | 1 | -1 | 0 | 30 | [6 empty] | Voltage | 0 | 0.85
34 | TRUE | TRUE | Q_up_1 | 1.0651 | 1 | FALSE | Q | 0 | -1 | 0 | 30 | [6 empty] | Voltage | 0 | 1.118
35 | TRUE | FALSE | Q_up_2 | 1.118 | 1 | FALSE | Q | 0 | -1 | 0 | 30 | [6 empty] | Voltage | 0 | 1.118
36 | TRUE | TRUE | Q_up_3 | 1.118 | 1 | FALSE | Q | 0 | -1 | 0 | 30 | [6 empty] | Voltage | 0 | 1.15
37 | TRUE | TRUE | Q_down_1 | 1.0651 | 1 | FALSE | Q | 0 | -1 | 0 | 30 | [6 empty] | Voltage | 0 | 0.968
38 | TRUE | TRUE | Q_down_2 | 0.968 | 1 | FALSE | Q | 0 | -1 | 0 | 30 | [6 empty] | Voltage | 0 | 0.9
39 | TRUE | TRUE | Q_down_3 | 0.9 | 1 | FALSE | Q | 0 | -1 | 0 | 30 | [6 empty] | Voltage | 0 | 0.85
40 | TRUE | FALSE | PQ_OE | 1.0651 | 1 | FALSE | Q | 0.33 | -1 | 0 | 300 | [6 empty] | Pctrl ref. | 0 | 0
41 | TRUE | FALSE | PQ_UE | 1.0651 | 1 | FALSE | Q | -0.33 | -1 | 0 | 300 | [6 empty] | Pctrl ref. | 0 | 0
42 | TRUE | TRUE | Q_control_up | 1.0651 | 1 | FALSE | Q | 0 | 3 | 12.1893 | 30 | [6 empty] | Qctrl ref. | 0 | 0.15 |  | Qctrl ref. | 15 | 0.33
43 | TRUE | TRUE | Q_control_down | 1.0651 | 1 | FALSE | Q | 0.33 | 3 | 12.1893 | 30 | [6 empty] | Qctrl ref. | 0 | -0.15 |  | Qctrl ref. | 15 | -0.33
44 | TRUE | TRUE | Qpf_ref | 1.0651 | 1 | FALSE | PF | 1 | 3 | 12.1893 | 30 | [6 empty] | Qctrl ref. | 0 | 0.95
45 | TRUE | TRUE | Qpf_p | 1.0651 | 1 | FALSE | PF | -0.95 | 3 | 12.1893 | 30 | [6 empty] | Pctrl ref. | 0 | 0
46 | TRUE | TRUE | Q(u)_wg | 1.0651 | 1 | FALSE | Q(U) | 1 | 3 | 12.1893 | 42 | [6 empty] | dVoltage | 0 | 0.052868 |  | dVoltage | 7 | 0 |  | dVoltage | 14 | -0.097132 |  | dVoltage | 21 | 0 |  | dVoltage | 28 | 0.026434 |  | dVoltage | 35 | -0.048566
47 | TRUE | TRUE | Q(u)_tuning | 1.0651 | 1 | FALSE | Q(U) | 1 | 13.5637 | 12.1893 | 42 | [6 empty] | dVoltage | 0 | 0.052868 |  | dVoltage | 7 | 0 |  | dVoltage | 14 | -0.097132 |  | dVoltage | 21 | 0 |  | dVoltage | 28 | 0.026434 |  | dVoltage | 35 | -0.048566
48 | TRUE | TRUE | Q(u)_sg | 1.0651 | 1 | FALSE | Q(U) | 1 | 14.3859 | 12.1152 | 42 | [6 empty] | dVoltage | 0 | 0.052868 |  | dVoltage | 7 | 0 |  | dVoltage | 14 | -0.097132 |  | dVoltage | 21 | 0 |  | dVoltage | 28 | 0.026434 |  | dVoltage | 35 | -0.048566
49 | TRUE | TRUE | LVFRT_profile | 1.0651 | 1 | FALSE | Default | 0 | -1 | 0 | 60 | [6 empty] | Voltage | 0 | 0 |  | Voltage | 0.15 | 0 | 0 | Voltage | 0.15 |  | 0 | Voltage | 0.15 |  | 0.62963 | Voltage | 1.5 |  | 0
50 | TRUE | TRUE | OVRT_profile | 1.0651 | 1 | FALSE | Default | 0 | -1 | 0 | 36 | [6 empty] | Voltage | 0 | 1.3 |  | Voltage | 0.1 | 1.2 |  | Voltage | 30.1 | 1
51 | TRUE | TRUE | Fault _rec_1 |  | 1 | FALSE | Default | 0 | -1 | 0 |  |  |  | caseInputFiles/DK1_fault1.csv
52 | TRUE | TRUE | Fault _rec_1_altq |  | 1 | FALSE | Q(U) | 1 | -1 | 0 |  |  |  | caseInputFiles/DK1_fault1.csv
53 | TRUE | TRUE | Fault _rec_2 |  | 1 | FALSE | Default | 0 | -1 | 0 |  |  |  | caseInputFiles/DK1_fault2.meas
54 | TRUE | TRUE | Fault _rec_2_alt |  | 1 | FALSE | Q(U) | 1 | -1 | 0 |  |  |  | caseInputFiles/DK1_fault2.meas
55 | TRUE | TRUE | Fault_3_0 | 1.0651 | 1 | FALSE | Default | 0 | 3 | 12.1893 | 30 | [6 empty] | 3p fault | 0 | 0% | 0.15
56 | TRUE | TRUE | Fault_3_25 | 1.0651 | 1 | FALSE | Default | 0 | 3 | 12.1893 | 30 | [6 empty] | 3p fault | 0 | 25% | 0.54706
57 | TRUE | TRUE | Fault_3_50 | 1.0651 | 1 | FALSE | Default | 0 | 3 | 12.1893 | 30 | [6 empty] | 3p fault | 0 | 50% | 0.94412
58 | TRUE | TRUE | Fault_3_75 | 1.0651 | 1 | FALSE | Default | 0 | 3 | 12.1893 | 30 | [6 empty] | 3p fault | 0 | 75% | 1.3412
59 | TRUE | TRUE | Fault_3_thres | 1.0651 | 1 | FALSE | Default | 0 | 3 | 12.1893 | 30 | [6 empty] | 3p fault | 0 | 85% | 1.5
60 | TRUE | TRUE | Fault_2_0 | 1.0651 | 1 | FALSE | Default | 0 | 3 | 12.1893 | 30 | [6 empty] | 2p-g fault | 0 | 0% | 0.15
61 | TRUE | TRUE | Fault_2_25 | 1.0651 | 1 | FALSE | Default | 0 | 3 | 12.1893 | 30 | [6 empty] | 2p-g fault | 0 | 25% | 0.54706
62 | TRUE | TRUE | Fault_2_50 | 1.0651 | 1 | FALSE | Default | 0 | 3 | 12.1893 | 30 | [6 empty] | 2p-g fault | 0 | 50% | 0.94412
63 | TRUE | TRUE | Fault_2_75 | 1.0651 | 1 | FALSE | Default | 0 | 3 | 12.1893 | 30 | [6 empty] | 2p-g fault | 0 | 75% | 1.3412
64 | TRUE | TRUE | Fault_2_thres | 1.0651 | 1 | FALSE | Default | 0 | 3 | 12.1893 | 30 | [6 empty] | 2p-g fault | 0 | 85% | 1.5
65 | TRUE | TRUE | Fault_1_0 | 1.0651 | 1 | FALSE | Default | 0 | 3 | 12.1893 | 30 | [6 empty] | 1p fault | 0 | 0% | 0.15
66 | TRUE | TRUE | Fault_1_25 | 1.0651 | 1 | FALSE | Default | 0 | 3 | 12.1893 | 30 | [6 empty] | 1p fault | 0 | 25% | 0.54706
67 | TRUE | TRUE | Fault_1_50 | 1.0651 | 1 | FALSE | Default | 0 | 3 | 12.1893 | 30 | [6 empty] | 1p fault | 0 | 50% | 0.94412
68 | TRUE | TRUE | Fault_1_75 | 1.0651 | 1 | FALSE | Default | 0 | 3 | 12.1893 | 30 | [6 empty] | 1p fault | 0 | 75% | 1.3412
69 | TRUE | TRUE | Fault_1_thres | 1.0651 | 1 | FALSE | Default | 0 | 3 | 12.1893 | 30 | [6 empty] | 1p fault | 0 | 85% | 1.5
70 | TRUE | TRUE | Fault_3_restrike | 1.0651 | 1 | FALSE | Default | 0 | 3 | 12.1893 | 30 | [6 empty] | 3p fault | 0 | 0% | 0.15 | 3p fault | 0.35 | 0 | 0.15
71 | TRUE | TRUE | Fault_1_restrike | 1.0651 | 1 | FALSE | Default | 0 | 3 | 12.1893 | 30 | [6 empty] | 1p fault | 0 | 0% | 0.15 | 1p fault | 0.35 | 0 | 0.15
72 | TRUE | TRUE | MaxPhaseJump | 1.0651 | 1 | FALSE | Default | 0 | 3 | 12.1893 | 10 | [6 empty] | Phase | 0 | 20 |  | Phase | 2.5 | 0 |  | Phase | 5 | -20 |  | Phase | 7.5 | 0
73 | TRUE | TRUE | MaxRoCoF | 1.0651 | 0.7 | FALSE | Default | 0 | 3 | 12.1893 | 5 | [6 empty] | Frequency | 0 |  | -2 | Frequency | 1.25 |  | 2 | Frequency | 3.25 |  | -2 | Frequency | 4
74 | FALSE | TRUE | MTB_TEST_1 | 1.0651 | 0.7 | FALSE | Default | 0 | -1 | 0 |  |  |  |  | caseInputFiles/KAS_emt_fault.out
75 | FALSE | TRUE | MTB_TEST_2 | 1.0651 | 0.7 | FALSE | Default | 0 | 3 | 12.1893 | 7 | [6 empty] | Frequency | 0 | 50 |  | SCR | 3.5 | 1 |  | dVoltage | 2 | 1 |  | 3p fault | 3 | 0 | 1

## Event types
| Description | X1 description | X1 unit | X2 description | X2 unit
Pctrl ref. | Pref change | setpoint, base Pn | pu | gradient | 1/s
Qctrl ref. | Qref change | setpoint, base Pn | pu | gradient | 1/s
Voltage | Grid voltage change (behind grid impedance) | setpoint, base Un | pu | gradient | 1/s
dVoltage | Delta grid voltage change (behind grid impedance) | setpoint, base Un | pu | gradient | 1/s
Phase | Grid phase change (behind grid impedance) | setpoint | degree | gradient | degree/s
Frequency | Grid frequency change | setpoint | Hz | gradient | Hz/s
SCR | Grid impedance change | SCR | - | X/R | -
3p fault | Three phase fault | residual voltage (across fault reactance), base Un | pu | fault time | s
2p-g fault | Two phase to ground fault | residual voltage (across fault reactance), base Un | pu | fault time | s
2p fault | Two phase fault | residual voltage (across fault reactance), base Un | pu | fault time | s
1p fault | One phase fault | residual voltage (across fault reactance), base Un | pu | fault time | s
3p fault (ohm) | Three phase fault | fault resistance | ohm | fault reactance | ohm
2p-g fault (ohm) | Two phase to ground fault | fault resistance | ohm | fault reactance | ohm
2p fault (ohm) | Two phase fault | fault resistance | ohm | fault reactance | ohm
1p fault (ohm) | One phase fault | fault resistance | ohm | fault reactance | ohm
Clear fault | Clear any fault | N/A | N/A | N/A | N/A

## datavalidation (hidden)
DK1 | Q | Max
DK2 | PF | Min
| Q(U) | Tuning
| Default | Ideal