## Settings
Range
Projectname | Solbakken
PSCAD Namespace | Solbakken
Pn | 26 | MW
Uc | 62.5 | kV
Un | 62.5 | kV
Area | DK1
SCR min | 8 | -
SCR tuning | 16.36 | -
SCR max | 17.84 | -
V droop | 2 | %
X/R SCR min | 23.1451 | -
X/R SCR tuning | 23.1451 | -
X/R SCR max | 23.1451 | -
R0 | 0 | ohm
X0 | 0 | ohm
Default Q mode | Q | - | Qmode signal from MTB is constant. Qref mode == 0, Q(U) mode == 1 and Qpf == 2.
PSCAD Timestep | 2 | µs
PSCAD Initialization time | 3 | s
PSCAD Kp | 1.4 | -
PSCAD Ti | 0.007 | 1/s
PF flat time | 0.1 | s
PF variable step | TRUE | -
PF enforced sync. | TRUE | -
PF force asymmetrical sim. | FALSE | -
PF enforce P limits in LDF | TRUE | - | Can be neccesary to turn off when QDSL is utilized for initialization.
PF enforce Q limits in LDF | TRUE | - | Can be neccesary to turn off when QDSL is utilized for initialization.

## Area values
| DK1 |  |  | DK2
Un | <110 kV | 110 kV <= Un < 300 kV | 300 kV <= Un | <110 kV | 110 kV <= Un < 300 kV | 300 kV <= Un | Selected
Power-frequency control
LFSM-O start (Hz) | 50.2 | 50.2 | 50.2 | 50.5 | 50.5 | 50.5 | 50.2
LFSM-O droop (%) | 5 | 5 | 5 | 4 | 4 | 4 | 5
LFSM-U start (Hz) | 49.8 | 49.8 | 49.8 | 49.5 | 49.5 | 49.5 | 49.8
LFSM-U droop (%) | 5 | 5 | 5 | 4 | 4 | 4 | 5
FSM deadband (Hz) | 0 | 0 | 0 | 0 | 0 | 0 | 0
FSM droop (%) | 6 | 6 | 6 | 6 | 6 | 6 | 6
FSM provision (%Pn) | 10 | 10 | 10 | 10 | 10 | 10 | 10
30min operation Fmax | 51.5 | 51.5 | 51.5 | 51.5 | 51.5 | 51.5 | 51.5
30min operation Fmin | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5
Reactive power capability (base Uc)
UQ Q=0pu Umax | 1.05 | 1.118 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05
UQ Q=0pu Umin | 0.9 | 0.968 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
UQ Q=+0.33pu Umax | 1.04 | 1.108 | 1.04 | 1.04 | 1.04 | 1.04 | 1.04
UQ Q=+0.33pu Umin | 0.9 | 0.968 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
UQ Q=-0.33pu Umax | 1.05 | 1.118 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05
UQ Q=-0.33pu Umin | 0.96 | 1.028 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
Cont. operation Umax | 1.1 | 1.118 | 1.05 | 1.1 | 1.05 | 1.05 | 1.1
Cont. operation Umin | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
60min operation Umax | 1.1 | 1.15 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
60min operation Umin | 0.9 | 0.85 | 0.85 | 0.9 | 0.9 | 0.9 | 0.9
LVFRT
LVFT start | 0.9 | 0.85 | 0.85 | 0.9 | 0.9 | 0.9 | 0.9
LVFRT stop | 0.9 | 0.85 | 0.85 | 0.9 | 0.9 | 0.9 | 0.9
Ures | 0.15 | 0 | 0 | 0.15 | 0 | 0 | 0.15
tclear | 0.25 | 0.15 | 0.15 | 0.25 | 0.15 | 0.15 | 0.25
Uclear | 0.15 | 0 | 0 | 0.15 | 0 | 0 | 0.15
trec1 | 0.25 | 0.15 | 0.15 | 0.25 | 0.15 | 0.15 | 0.25
Urec1 | 0.15 | 0 | 0 | 0.15 | 0 | 0 | 0.15
trec2 | 0.25 | 0.15 | 0.15 | 0.25 | 0.15 | 0.15 | 0.25
Urec2 | 0.9 | 0.85 | 0.85 | 0.9 | 0.9 | 0.9 | 0.9
trec3 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
OVRT
U1 | 1.2 | 1.3 | 1.3 | 1.2 | 1.3 | 1.3 | 1.2
t1 | 5 | 0.1 | 0.1 | 5 | 0.1 | 0.1 | 5
U2 | 1.15 | 1.2 | 1.2 | 1.15 | 1.2 | 1.2 | 1.15
t2 | 60 | 30 | 30 | 60 | 30 | 30 | 60

## Cases
[12 empty] | Event 1 |  |  |  | Event 2 |  |  |  | Event 3 |  |  |  | Event 4 |  |  |  | Event 5 |  |  |  | Event 6 |  |  |  | Event 7 |  |  |  | Event 8 |  |  |  | Event 9 |  |  |  | Event 10 |  |  |  | Event 11 |  |  |  | Event 12
Rank | RMS | EMT | Name | U0 | P0 | FSM | Qmode | Qref0 | SCR0 | XR0 | Simulationtime | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2 | type | time | X1 | X2
1 | TRUE | TRUE | SS_Q1 | 1 | 0 | FALSE | Q | 0 | 8 | 23.1451 | 60 | PF disconnect all ref.
2 | TRUE | TRUE | SS_Q2 | 1 | 0.5 | FALSE | Q | 0.2 | 8 | 23.1451 | 60 | PF disconnect all ref.
3 | TRUE | TRUE | SS_Q3 | 1 | 0.5 | FALSE | Q | -0.2 | 8 | 23.1451 | 60 | PF disconnect all ref.
4 | TRUE | TRUE | SS_Q4 | 1 | 1 | FALSE | Q | 0.33 | 8 | 23.1451 | 60 | PF disconnect all ref.
5 | TRUE | TRUE | SS_Q5 | 1 | 1 | FALSE | Q | -0.33 | 8 | 23.1451 | 60 | PF disconnect all ref.
6 | TRUE | TRUE | SS_Uctrl1 | 0.9 | 0.7 | FALSE | Q(U) | 1 | -1 | 0 | 60 | PF disconnect all ref.
7 | TRUE | TRUE | SS_Uctrl2 | 1.05 | 0.7 | FALSE | Q(U) | 1 | -1 | 0 | 60 | PF disconnect all ref.
8 | TRUE | TRUE | SS_PFctrl | 1 | 0.7 | FALSE | PF | 0.949 | 8 | 23.1451 | 60 | PF disconnect all ref.
9 | TRUE | FALSE | P_step_up_0.0_0.5 | 1 | 0 | FALSE | Default | 0 | 8 | 23.1451 | 155 | Pref | 0 | 0.5 | 0
10 | TRUE | TRUE | P_step_up_0.5_0.7 | 1 | 0.5 | FALSE | Default | 0 | 8 | 23.1451 | 65 | Pref | 0 | 0.7 | 0
11 | TRUE | FALSE | P_step_up_0.7_1.0 | 1 | 0.7 | FALSE | Default | 0 | 8 | 23.1451 | 95 | Pref | 0 | 1 | 0
12 | TRUE | FALSE | P_step_down_1.0_0.7 | 1 | 1 | FALSE | Default | 0 | 8 | 23.1451 | 95 | Pref | 0 | 0.7 | 0
13 | TRUE | FALSE | P_step_down_0.7_0.5 | 1 | 0.7 | FALSE | Default | 0 | 8 | 23.1451 | 65 | Pref | 0 | 0.5 | 0
14 | TRUE | FALSE | P_step_down_0.5_0.0 | 1 | 0.5 | FALSE | Default | 0 | 8 | 23.1451 | 155 | Pref | 0 | 0 | 0
15 | TRUE | TRUE | FSM_step | 1 | 0.7 | TRUE | Default | 0 | 8 | 23.1451 | 48 | Frequency | 0 | 50.199 |  | Frequency | 8 | 50 |  | Frequency | 16 | 49.801 |  | Frequency | 24 | 50 |  | Frequency | 32 | 50.15 |  | Frequency | 40 | 49.85
16 | TRUE | TRUE | FSM_LFSMO_ramp | 1 | 0.5 | TRUE | Default | 0 | 8 | 23.1451 | 40 | Frequency | 0 | 50 | 0.0725 | Frequency | 30 | 50
17 | TRUE | TRUE | FSM_LFSMU_ramp | 1 | 0.5 | TRUE | Default | 0 | 8 | 23.1451 | 40 | Frequency | 0 | 50 | -0.0725 | Frequency | 30 | 50
18 | TRUE | TRUE | FSM_rec_pstep | 1 | 0.7 | TRUE | Default | 0 | 8 | 23.1451 |  | Frequency recording |  | recordings/DK1_frekvens.meas | 1 | Pref | 1 | 0 | 0
19 | TRUE | TRUE | LFSM-OU_step | 1 | 0.5 | FALSE | Default | 0 | 8 | 23.1451 | 60 | Frequency | 0 | 50.45 |  | Frequency | 8 | 50 |  | Frequency | 16 | 49.55 |  | Frequency | 24 | 50 |  | Frequency | 32 | 51.05 |  | Frequency | 46 | 51.45
20 | TRUE | TRUE | LFSMO_ramp+pstep | 1 | 0.5 | FALSE | Default | 0 | 8 | 23.1451 | 40 | Frequency | 0 |  | 0.075 | Frequency | 20 |  | 0 | Pref | 2 | 1
21 | TRUE | TRUE | LFSMU_ramp | 1 | 0.5 | FALSE | Default | 0 | 8 | 23.1451 | 40 | Frequency | 0 |  | -0.125 | Frequency | 20 |  | 0
22 | TRUE | TRUE | U-Q/Pn_N_up | 1 | 1 | FALSE | Q | 0 | -1 | 0 | 50 | Voltage | 0 | 1.05
23 | TRUE | TRUE | U-Q/Pn_N_down | 1 | 1 | FALSE | Q | 0 | -1 | 0 | 50 | Voltage | 0 | 0.9
24 | TRUE | TRUE | U-Q/Pn_UE_up | 1 | 1 | FALSE | Q | -0.33 | -1 | 0 | 50 | Voltage | 0 | 1.05
25 | TRUE | TRUE | U-Q/Pn_UE_down | 1 | 1 | FALSE | Q | -0.33 | -1 | 0 | 50 | Voltage | 0 | 0.96
26 | TRUE | TRUE | U-Q/Pn_OE_up | 1 | 1 | FALSE | Q | 0.33 | -1 | 0 | 50 | Voltage | 0 | 1.04
27 | TRUE | TRUE | U-Q/Pn_OE_down | 1 | 1 | FALSE | Q | 0.33 | -1 | 0 | 50 | Voltage | 0 | 0.9
28 | TRUE | TRUE | Q(u)_up_1 | 1 | 1 | FALSE | Q(U) | 1 | -1 | 0 | 30 | Voltage | 0 | 1.05
29 | TRUE | TRUE | Q(u)_up_2 | 1.05 | 1 | FALSE | Q(U) | 1 | -1 | 0 | 30 | Voltage | 0 | 1.1
30 | TRUE | FALSE | Q(u)_up_3 | 1.1 | 1 | FALSE | Q(U) | 1 | -1 | 0 | 30 | Voltage | 0 | 1.1
31 | TRUE | TRUE | Q(u)_down_1 | 1 | 1 | FALSE | Q(U) | 1 | -1 | 0 | 30 | Voltage | 0 | 0.9
32 | TRUE | FALSE | Q(u)_down_2 | 0.9 | 1 | FALSE | Q(U) | 1 | -1 | 0 | 30 | Voltage | 0 | 0.9
33 | TRUE | FALSE | Q(u)_down_3 | 0.9 | 1 | FALSE | Q(U) | 1 | -1 | 0 | 30 | Voltage | 0 | 0.9
34 | TRUE | TRUE | Q_up_1 | 1 | 1 | FALSE | Q | 0 | -1 | 0 | 30 | Voltage | 0 | 1.05
35 | TRUE | TRUE | Q_up_2 | 1.05 | 1 | FALSE | Q | 0 | -1 | 0 | 30 | Voltage | 0 | 1.1
36 | TRUE | FALSE | Q_up_3 | 1.1 | 1 | FALSE | Q | 0 | -1 | 0 | 30 | Voltage | 0 | 1.1
37 | TRUE | TRUE | Q_down_1 | 1 | 1 | FALSE | Q | 0 | -1 | 0 | 30 | Voltage | 0 | 0.9
38 | TRUE | FALSE | Q_down_2 | 0.9 | 1 | FALSE | Q | 0 | -1 | 0 | 30 | Voltage | 0 | 0.9
39 | TRUE | FALSE | Q_down_3 | 0.9 | 1 | FALSE | Q | 0 | -1 | 0 | 30 | Voltage | 0 | 0.9
40 | TRUE | FALSE | PQ_OE | 1 | 1 | FALSE | Q | 0.33 | -1 | 0 | 300 | Pref | 0 | 0
41 | TRUE | FALSE | PQ_UE | 1 | 1 | FALSE | Q | -0.33 | -1 | 0 | 300 | Pref | 0 | 0
42 | TRUE | TRUE | Q_control_up | 1 | 1 | FALSE | Q | 0 | 8 | 23.1451 | 30 | Qref | 0 | 0.15 |  | Qref | 15 | 0.33
43 | TRUE | TRUE | Q_control_down | 1 | 1 | FALSE | Q | 0.33 | 8 | 23.1451 | 30 | Qref | 0 | -0.15 |  | Qref | 15 | -0.33
44 | TRUE | TRUE | Qpf_ref | 1 | 1 | FALSE | PF | 1 | 8 | 23.1451 | 30 | Qref | 0 | 0.95
45 | TRUE | TRUE | Qpf_p | 1 | 1 | FALSE | PF | -0.95 | 8 | 23.1451 | 30 | Pref | 0 | 0
46 | TRUE | TRUE | Q(u)_wg | 1 | 1 | FALSE | Q(U) | 1 | 8 | 23.1451 | 42 | dVoltage | 0 | 0.05 |  | dVoltage | 7 | 0 |  | dVoltage | 14 | -0.1 |  | dVoltage | 21 | 0 |  | dVoltage | 28 | 0.025 |  | dVoltage | 35 | -0.05
47 | TRUE | TRUE | Q(u)_tuning | 1 | 1 | FALSE | Q(U) | 1 | 16.36 | 23.1451 | 42 | dVoltage | 0 | 0.05 |  | dVoltage | 7 | 0 |  | dVoltage | 14 | -0.1 |  | dVoltage | 21 | 0 |  | dVoltage | 28 | 0.025 |  | dVoltage | 35 | -0.05
48 | TRUE | TRUE | Q(u)_sg | 1 | 1 | FALSE | Q(U) | 1 | 17.84 | 23.1451 | 42 | dVoltage | 0 | 0.05 |  | dVoltage | 7 | 0 |  | dVoltage | 14 | -0.1 |  | dVoltage | 21 | 0 |  | dVoltage | 28 | 0.025 |  | dVoltage | 35 | -0.05
49 | TRUE | TRUE | LVFRT_profile | 1 | 1 | FALSE | Default | 0 | -1 | 0 | 60 | Voltage | 0 | 0.15 | 0 | Voltage | 0.25 | 0.15 | 0 | Voltage | 0.25 | 0.15 | 0 | Voltage | 0.25 | 0.15 | 0.6 | Voltage | 1.5 | 0.9 | 0
50 | TRUE | TRUE | OVRT_profile | 1 | 1 | FALSE | Default | 0 | -1 | 0 | 70 | Voltage | 0 | 1.2 |  | Voltage | 5 | 1.15 |  | Voltage | 65 | 1
51 | TRUE | TRUE | Fault _rec_1 | 1 | 1 | FALSE | Default | 0 | -1 | 0 |  | Voltage recording |  | recordings/DK1_fault1.csv | 1
52 | TRUE | TRUE | Fault _rec_1_altq | 1 | 1 | FALSE | Q(U) | 1 | -1 | 0 |  | Voltage recording |  | recordings/DK1_fault1.csv | 1
53 | TRUE | TRUE | Fault _rec_2 | 1 | 1 | FALSE | Default | 0 | -1 | 0 |  | Voltage recording |  | recordings/DK1_fault2.meas | 1
54 | TRUE | TRUE | Fault _rec_2_alt | 1 | 1 | FALSE | Q(U) | 1 | -1 | 0 |  | Voltage recording |  | recordings/DK1_fault2.meas | 1
55 | TRUE | TRUE | Fault_3_0 | 1 | 1 | FALSE | Default | 0 | 8 | 23.1451 | 30 | 3p fault | 0 | 15% | 0.25
56 | TRUE | TRUE | Fault_3_25 | 1 | 1 | FALSE | Default | 0 | 8 | 23.1451 | 30 | 3p fault | 0 | 25% | 0.41667
57 | TRUE | TRUE | Fault_3_50 | 1 | 1 | FALSE | Default | 0 | 8 | 23.1451 | 30 | 3p fault | 0 | 50% | 0.83333
58 | TRUE | TRUE | Fault_3_75 | 1 | 1 | FALSE | Default | 0 | 8 | 23.1451 | 30 | 3p fault | 0 | 75% | 1.25
59 | TRUE | TRUE | Fault_3_thres | 1 | 1 | FALSE | Default | 0 | 8 | 23.1451 | 30 | 3p fault | 0 | 90% | 1.5
60 | TRUE | TRUE | Fault_2_0 | 1 | 1 | FALSE | Default | 0 | 8 | 23.1451 | 30 | 2p-g fault | 0 | 15% | 0.25
61 | TRUE | TRUE | Fault_2_25 | 1 | 1 | FALSE | Default | 0 | 8 | 23.1451 | 30 | 2p-g fault | 0 | 25% | 0.41667
62 | TRUE | TRUE | Fault_2_50 | 1 | 1 | FALSE | Default | 0 | 8 | 23.1451 | 30 | 2p-g fault | 0 | 50% | 0.83333
63 | TRUE | TRUE | Fault_2_75 | 1 | 1 | FALSE | Default | 0 | 8 | 23.1451 | 30 | 2p-g fault | 0 | 75% | 1.25
64 | TRUE | TRUE | Fault_2_thres | 1 | 1 | FALSE | Default | 0 | 8 | 23.1451 | 30 | 2p-g fault | 0 | 90% | 1.5
65 | TRUE | TRUE | Fault_1_0 | 1 | 1 | FALSE | Default | 0 | 8 | 23.1451 | 30 | 1p fault | 0 | 15% | 0.25
66 | TRUE | TRUE | Fault_1_25 | 1 | 1 | FALSE | Default | 0 | 8 | 23.1451 | 30 | 1p fault | 0 | 25% | 0.41667
67 | TRUE | TRUE | Fault_1_50 | 1 | 1 | FALSE | Default | 0 | 8 | 23.1451 | 30 | 1p fault | 0 | 50% | 0.83333
68 | TRUE | TRUE | Fault_1_75 | 1 | 1 | FALSE | Default | 0 | 8 | 23.1451 | 30 | 1p fault | 0 | 75% | 1.25
69 | TRUE | TRUE | Fault_1_thres | 1 | 1 | FALSE | Default | 0 | 8 | 23.1451 | 30 | 1p fault | 0 | 90% | 1.5
70 | TRUE | TRUE | Fault_3_restrike | 1 | 1 | FALSE | Default | 0 | 8 | 23.1451 | 30 | 3p fault | 0 | 15% | 0.25 | 3p fault | 0.45 | 0.15 | 0.25
71 | TRUE | TRUE | Fault_1_restrike | 1 | 1 | FALSE | Default | 0 | 8 | 23.1451 | 30 | 1p fault | 0 | 15% | 0.25 | 1p fault | 0.45 | 0.15 | 0.25
72 | TRUE | TRUE | MaxPhaseJump | 1 | 1 | FALSE | Default | 0 | 8 | 23.1451 | 10 | Phase | 0 | 20 |  | Phase | 2.5 | 0 |  | Phase | 5 | -20 |  | Phase | 7.5 | 0
73 | TRUE | TRUE | MaxRoCoF | 1 | 0.7 | FALSE | Default | 0 | 8 | 23.1451 | 5 | Frequency | 0 | 50 | -2 | Frequency | 1.25 |  | 2 | Frequency | 3.25 |  | -2 | Frequency | 4
74 | TRUE | TRUE | SCR_step | 1 | 1 | FALSE | Default | 0 | 17.84 | 23.1451 | 10 | SCR | 0 | 8 |  | SCR | 5 | 17.84 | 23.1451
75 | TRUE | TRUE | SCR_step_altq | 1 | 1 | FALSE | Q(U) | 1 | 17.84 | 23.1451 | 10 | SCR | 0 | 8 |  | SCR | 5 | 17.84 | 23.1451
76 | TRUE | TRUE | Fault_SCR | 1 | 1 | FALSE | Default | 0 | 17.84 | 23.1451 | 10 | 3p fault | 0 | 0 | 0.1 | SCR | 0.099 | 8 | 23.1451
77 | TRUE | TRUE | Fault_SCR_altq | 1 | 1 | FALSE | Q(U) | 1 | 17.84 | 23.1451 | 10 | 3p fault | 0 | 0 | 0.1 | SCR | 0.099 | 8 | 23.1451
78 | TRUE | TRUE | Fault_SCR_freq | 1 | 1 | FALSE | Default | 0 | 17.84 | 23.1451 | 30 | 3p fault | 0 | 0 | 0.1 | SCR | 0.099 | 8 | 23.1451 | Frequency | 0.05 | 51
79 | TRUE | TRUE | MTB_TEST_1 | 1 | 0.7 | FALSE | Default | 0 | -1 | 0 |  | Inst. Voltage recording |  | recordings/KAS_emt_fault.out | 1 | Voltage recording |  | recordings/DK1_fault1.csv | 1
80 | TRUE | TRUE | MTB_TEST_2 | 1 | 0.7 | FALSE | Default | 0 | 8 | 0 |  | Qref recording |  | recordings/DK1_fault1.csv | 1 | Signal 5 | 0.3 |  | -10 | Signal 5 | 1.3 |  | 0 | Voltage | 2 | 0.5 |  | 3p fault | 2 | 0.4 | 0.1 | 1p fault (ohm) | 2.5 | 0 | 0.01 | Clear fault | 3

## Event types
| Description | X1 description | X1 unit | X2 description | X2 unit
Pref | Pref change | setpoint, base Pn | pu | gradient | 1/s
Qref | Qref change | setpoint, base Pn | pu | gradient | 1/s
Voltage | Grid voltage change (thevenin) | setpoint, base Un | pu | gradient | 1/s
dVoltage | Delta grid voltage change (thevenin) | setpoint, base Un | pu | gradient | 1/s
Phase | Grid phase change (thevenin) | setpoint | degree | gradient | degree/s
Frequency | Grid frequency change | setpoint | Hz | gradient | Hz/s
SCR | Grid impedance change | SCR | - | X/R | -
3p fault | Three phase fault | residual voltage (across fault reactance), base Un | pu | fault time | s
2p-g fault | Two phase to ground fault | residual voltage (across fault reactance), base Un | pu | fault time | s
2p fault | Two phase fault | residual voltage (across fault reactance), base Un | pu | fault time | s
1p fault | One phase fault | residual voltage (across fault reactance), base Un | pu | fault time | s
3p fault (ohm) | Three phase fault | fault resistance | ohm | fault reactance | ohm
2p-g fault (ohm) | Two phase to ground fault | fault resistance | ohm | fault reactance | ohm
2p fault (ohm) | Two phase fault | fault resistance | ohm | fault reactance | ohm
1p fault (ohm) | One phase fault | fault resistance | ohm | fault reactance | ohm
Clear fault | Clear any fault | N/A | N/A | N/A | N/A
Pref recording | Use external measurement file for Pref signal. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Qref recording | Use external measurement file for Qref signal. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Voltage recording | Use external measurement file for the thevenin voltage signal (RMS). First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Inst. Voltage recording | Only supported for PSCAD. Use external measurement file for the thevenin instantaneous voltages. Time value ignored. | Relative path to measurementfile | N/A | Scaling factor | -
Phase recording | Use external measurement file for the thevenin voltage phase signal. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Frequency recording | Use external measurement file for the thevenin voltage frequency signal. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 1 | Custom signal 1 change | value | ? | gradient | ?/s
Signal 2 | Custom signal 2 change | value | ? | gradient | ?/s
Signal 3 | Custom signal 3 change | value | ? | gradient | ?/s
Signal 4 | Custom signal 4 change | value | ? | gradient | ?/s
Signal 5 | Custom signal 5 change | value | ? | gradient | ?/s
Signal 6 | Custom signal 6 change | value | ? | gradient | ?/s
Signal 7 | Custom signal 7 change | value | ? | gradient | ?/s
Signal 8 | Custom signal 8 change | value | ? | gradient | ?/s
Signal 9 | Custom signal 9 change | value | ? | gradient | ?/s
Signal 10 | Custom signal 10 change | value | ? | gradient | ?/s
Signal 1 recording | Use external measurement file for custom signal 1. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 2 recording | Use external measurement file for custom signal 2. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 3 recording | Use external measurement file for custom signal 3. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 4 recording | Use external measurement file for custom signal 4. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 5 recording | Use external measurement file for custom signal 5. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 6 recording | Use external measurement file for custom signal 6. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 7 recording | Use external measurement file for custom signal 7. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 8 recording | Use external measurement file for custom signal 8. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 9 recording | Use external measurement file for custom signal 9. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
Signal 10 recording | Use external measurement file for custom signal 10. First value hold until flattime or initialtime has elapsed. | Relative path to measurementfile | N/A | Scaling factor | -
PF disconnect all ref. | In Powerfactory out-of-service all references (including custom signals) to plant. For initialization testing purposes. | N/A | N/A | N/A | N/A
PF force asymmetrical | Force case to be simulated asymmetricaly. | N/A | N/A | N/A | N/A

## datavalidation
DK1 | Q | Max | TRUE
DK2 | PF | Min | FALSE
| Q(U) | Tuning
| Default | Ideal