## Input
Range
ProjectName | BS
Pn | 55.5 | MW
Uc | 62.5 | kV
Un | 60 | kV
Area | DK1
SCR min | 13.5637 | -
SCR tuning | 13.5637 | -
SCR max | 14.3859 | -
X/R SCR min | 12.1893 | -
X/R SCR tuning | 12.1893 | -
X/R SCR max | 12.1152 | -
R0 | 0 | pu
X0 | 0 | pu
Default Q mode | Q | -
Q(u) droop | 2 | % | 2-7
PSCAD Timestep | 2 | µs
Volley | 8 | -
Case time offset | 3 | s
U> | 1.1 | p.u.
U> time | 60 | s
U>> | 1.15 | p.u.
U>> time | 0.2 | s
U>>> | 1.2 | p.u.
U>>> time | 0.1 | s
U< | 0.9 | p.u.
U< time | 60 | s
f> | 51.5 | Hz
f> time | 0.2 | s
f< | 47.5 | Hz
f< time | 0.2 | s
df/dt pos | 2.5 | Hz/s
df/dt pos time | 0.08 | s
df/dt neg | -2.5 | Hz/s
df/dt neg time | 0.08 | s

## Area values
| DK1 |  |  | DK2
Un | <110 kV | 110 kV <= Un < 300 kV | 300 kV <= Un | <110 kV | 110 kV <= Un < 300 kV | 300 kV <= Un | Selected
Power-frequency control
LFSM-O start (Hz) | 50.2 | 50.2 | 50.2 | 50.5 | 50.5 | 50.5 | 50.2
LFSM-O droop (%) | 5 | 5 | 5 | 4 | 4 | 4 | 5
LFSM-U start (Hz) | 49.8 | 49.8 | 49.8 | 49.5 | 49.5 | 49.5 | 49.8
LFSM-U droop (%) | 5 | 5 | 5 | 4 | 4 | 4 | 5
FSM deadband (Hz) | 0 | 0 | 0 | 0 | 0 | 0 | 0
FSM droop (%) | 6 | 6 | 6 | 6 | 6 | 6 | 6
FSM provision (%Pn) | 10 | 10 | 10 | 10 | 10 | 10 | 10
30min operation Fmax | 51.5 | 51.5 | 51.5 | 51.5 | 51.5 | 51.5 | 51.5
30min operation Fmin | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5
Reactive power capability (base Uc)
UQ Q=0pu Umax | 1.05 | 1.0733 | 1.008 | 1.05 | 1.008 | 1.008 | 1.05
UQ Q=0pu Umin | 0.9 | 0.92928 | 0.864 | 0.9 | 0.864 | 0.864 | 0.9
UQ Q=+0.33pu Umax | 1.04 | 1.0637 | 0.9984 | 1.04 | 0.9984 | 0.9984 | 1.04
UQ Q=+0.33pu Umin | 0.9 | 0.92928 | 0.864 | 0.9 | 0.864 | 0.864 | 0.9
UQ Q=-0.33pu Umax | 1.05 | 1.0733 | 1.008 | 1.05 | 1.008 | 1.008 | 1.05
UQ Q=-0.33pu Umin | 0.96 | 0.98688 | 0.9216 | 0.96 | 0.9216 | 0.9216 | 0.96
Cont. operation Umax | 1.1 | 1.0733 | 1.008 | 1.1 | 1.008 | 1.008 | 1.1
Cont. operation Umin | 0.9 | 0.864 | 0.864 | 0.9 | 0.864 | 0.864 | 0.9
60min operation Umax | 1.1 | 1.104 | 1.056 | 1.1 | 1.056 | 1.056 | 1.1
60min operation Umin | 0.9 | 0.816 | 0.816 | 0.9 | 0.864 | 0.864 | 0.9
LVFRT
LVFT start | 0.9 | 0.816 | 0.816 | 0.9 | 0.864 | 0.864 | 0.9
LVFRT stop | 0.9 | 0.816 | 0.816 | 0.9 | 0.864 | 0.864 | 0.9
Ures | 0.15 | 0 | 0 | 0.15 | 0 | 0 | 0.15
tclear | 0.25 | 0.15 | 0.15 | 0.25 | 0.15 | 0.15 | 0.25
Uclear | 0.15 | 0 | 0 | 0.15 | 0 | 0 | 0.15
trec1 | 0.25 | 0.15 | 0.15 | 0.25 | 0.15 | 0.15 | 0.25
Urec1 | 0.15 | 0 | 0 | 0.15 | 0 | 0 | 0.15
trec2 | 0.25 | 0.15 | 0.15 | 0.25 | 0.15 | 0.15 | 0.25
Urec2 | 0.9 | 0.816 | 0.816 | 0.9 | 0.864 | 0.864 | 0.9
trec3 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
OVRT
U1 | 1.2 | 1.248 | 1.248 | 1.2 | 1.248 | 1.248 | 1.2
t1 | 5 | 0.1 | 0.1 | 5 | 0.1 | 0.1 | 5
U2 | 1.15 | 1.152 | 1.152 | 1.15 | 1.152 | 1.152 | 1.15
t2 | 60 | 30 | 30 | 60 | 30 | 30 | 60

## Cases
[16 empty] | Event 1 |  |  |  | Event 2 |  |  |  | Event 3 |  |  |  | Event 4 |  |  |  | Event 5 |  |  |  | Event 6 |  |  |  | Event 7 |  |  |  | Event 8 |  |  |  | Event 9 |  |  |  | Event 10 |  |  |  | Event 11 |  |  |  | Event 12
Rank/Id | RMS | EMT | Name | U0 | P0 | FSM enabled | Qmode | Q ref. Initial | Simulationtime | SCR | Pctrl meas. File | Qctrl meas. File | Voltage meas. File | Phase meas. File | Frequency meas. File | type | time | Sp or res. U | ramp/periode | type | time | Sp or res. U | ramp/periode | type | time | Sp or res. U | ramp/periode | type | time | Sp or res. U | ramp/periode | type | time | Sp or res. U | ramp/periode | type | time | Sp or res. U | ramp/periode | type | time | Sp or res. U | ramp/periode | type | time | Sp or res. U | ramp/periode | type | time | Sp or res. U | ramp/periode | type | time | Sp or res. U | ramp/periode | type | time | Sp or res. U | ramp/periode | type | time | Sp or res. U | ramp/periode
1 | FALSE | TRUE | SS_Q1 | 1 | 0 | FALSE | Q | 0 | 60 | Min
2 | FALSE | TRUE | SS_Q2 | 1 | 0.5 | FALSE | Q | 0.2 | 60 | Min
3 | FALSE | TRUE | SS_Q3 | 1 | 0.5 | FALSE | Q | -0.2 | 60 | Min
4 | FALSE | TRUE | SS_Q4 | 1 | 1 | FALSE | Q | 0.33 | 60 | Min
5 | FALSE | TRUE | SS_Q5 | 1 | 1 | FALSE | Q | -0.3 | 60 | Min
6 | FALSE | TRUE | SS_Uctrl1 | 0.99 | 0.7 | FALSE | Q(U) | 1 | 60 | Min
7 | FALSE | TRUE | SS_Uctrl2 | 0.99 | 0.7 | FALSE | Q(U) | 1 | 60 | Min
8 | FALSE | TRUE | SS_PFctrl | 1.01 | 0.7 | FALSE | PF | 0.949 | 60 | Min
9 | FALSE | FALSE | P_step_up_0.0_0.5 | 1 | 0 | FALSE | Default | 0 | 155 | Min | [5 empty] | Pctrl ref. | 0 | 0.5 | 0
10 | FALSE | TRUE | P_step_up_0.5_0.7 | 1 | 0.5 | FALSE | Default | 0 | 65 | Min | [5 empty] | Pctrl ref. | 0 | 0.7 | 0
11 | FALSE | FALSE | P_step_up_0.7_1.0 | 1 | 0.7 | FALSE | Default | 0 | 95 | Min | [5 empty] | Pctrl ref. | 0 | 1 | 0
12 | FALSE | FALSE | P_step_down_1.0_0.7 | 1 | 1 | FALSE | Default | 0 | 95 | Min | [5 empty] | Pctrl ref. | 0 | 0.7 | 0
13 | FALSE | FALSE | P_step_down_0.7_0.5 | 1 | 0.7 | FALSE | Default | 0 | 65 | Min | [5 empty] | Pctrl ref. | 0 | 0.5 | 0
14 | FALSE | FALSE | P_step_down_0.5_0.0 | 1 | 0.5 | FALSE | Default | 0 | 155 | Min | [5 empty] | Pctrl ref. | 0 | 0 | 0
15 | FALSE | TRUE | FSM_step | 1 | 0.7 | TRUE | Default | 0 | 48 | Min | [5 empty] | Frequency | 0 | 50.199 |  |  | 8 | 50 |  |  | 16 | 49.801 |  |  | 24 | 50 |  |  | 32 | 50.15 |  |  | 40 | 49.85
16 | FALSE | TRUE | FSM_LFSMO_ramp | 1 | 0.5 | TRUE | Default | 0 | 40 | Min | [5 empty] | Frequency | 0 |  | 0.0725 |  | 30 | 50
17 | FALSE | TRUE | FSM_LFSMU_ramp | 1 | 0.5 | TRUE | Default | 0 | 40 | Min | [5 empty] | Frequency | 0 |  | -0.0725 |  | 30 | 50
18 | FALSE | TRUE | FSM_rec_pstep | 1 | 0.7 | TRUE | Default | 0 |  | Min |  |  |  |  | DK1_frekvens.csv | Pctrl ref. | 1 | 0 | 0
19 | FALSE | TRUE | LFSM-OU_step | 1 | 0.5 | FALSE | Default | 0 | 60 | Min | [5 empty] | Frequency | 0 | 50.45 |  |  | 8 | 50 |  |  | 16 | 49.55 |  |  | 24 | 50 |  |  | 32 | 51.05 |  |  | 46 | 51.45
20 | TRUE | TRUE | LFSMO_ramp | 1 | 0.5 | FALSE | Default | 0 | 40 | Min | [5 empty] | Frequency | 0 |  | 0.075 |  | 20 |  | 0 | Pctrl ref. | 2 | 1
21 | FALSE | TRUE | LFSMU_ramp | 1 | 0.5 | FALSE | Default | 0 | 40 | Min | [5 empty] | Frequency | 0 |  | -0.125 |  | 20 |  | 0
22 | FALSE | TRUE | U-Q/Pn_N_up | 1 | 1 | FALSE | Q | 0 | 50 | Ideal | [5 empty] | Voltage | 0 | 1.05 |  |  | 40 | 1
23 | FALSE | TRUE | U-Q/Pn_N_down | 1 | 1 | FALSE | Q | 0 | 50 | Ideal | [5 empty] | Voltage | 0 | 0.9 |  |  | 40 | 1
24 | FALSE | TRUE | U-Q/Pn_UE_up | 1 | 1 | FALSE | Q | -0.33 | 50 | Ideal | [5 empty] | Voltage | 0 | 1.05 |  |  | 40 | 1
25 | FALSE | TRUE | U-Q/Pn_UE_down | 1 | 1 | FALSE | Q | -0.33 | 50 | Ideal | [5 empty] | Voltage | 0 | 0.96 |  |  | 40 | 1
26 | FALSE | TRUE | U-Q/Pn_OE_up | 1 | 1 | FALSE | Q | 0.33 | 50 | Ideal | [5 empty] | Voltage | 0 | 1.04 |  |  | 40 | 1
27 | FALSE | TRUE | U-Q/Pn_OE_down | 1 | 1 | FALSE | Q | 0.33 | 50 | Ideal | [5 empty] | Voltage | 0 | 0.9 |  |  | 40 | 1
28 | FALSE | TRUE | Q(u)_up_1 | 1 | 1 | FALSE | Q(U) | 1 | 30 | Ideal | [5 empty] | Voltage | 0 | 1.05
29 | FALSE | TRUE | Q(u)_up_2 | 1.05 | 1 | FALSE | Q(U) | 1 | 30 | Ideal | [5 empty] | Voltage | 0 | 1.1
30 | FALSE | FALSE | Q(u)_up_3 | 1.1 | 1 | FALSE | Q(U) | 1 | 30 | Ideal | [5 empty] | Voltage | 0 | 1.1
31 | FALSE | TRUE | Q(u)_down_1 | 1 | 1 | FALSE | Q(U) | 1 | 30 | Ideal | [5 empty] | Voltage | 0 | 0.9
32 | FALSE | FALSE | Q(u)_down_2 | 0.9 | 1 | FALSE | Q(U) | 1 | 30 | Ideal | [5 empty] | Voltage | 0 | 0.9
33 | FALSE | FALSE | Q(u)_down_3 | 0.9 | 1 | FALSE | Q(U) | 1 | 30 | Ideal | [5 empty] | Voltage | 0 | 0.9
34 | FALSE | TRUE | Q_up_1 | 1 | 1 | FALSE | Q | 1 | 30 | Ideal | [5 empty] | Voltage | 0 | 1.05
35 | FALSE | TRUE | Q_up_2 | 1.05 | 1 | FALSE | Q | 1 | 30 | Ideal | [5 empty] | Voltage | 0 | 1.1
36 | FALSE | FALSE | Q_up_3 | 1.1 | 1 | FALSE | Q | 1 | 30 | Ideal | [5 empty] | Voltage | 0 | 1.1
37 | FALSE | TRUE | Q_down_1 | 1 | 1 | FALSE | Q | 1 | 30 | Ideal | [5 empty] | Voltage | 0 | 0.9
38 | FALSE | FALSE | Q_down_2 | 0.9 | 1 | FALSE | Q | 1 | 30 | Ideal | [5 empty] | Voltage | 0 | 0.9
39 | FALSE | FALSE | Q_down_3 | 0.9 | 1 | FALSE | Q | 1 | 30 | Ideal | [5 empty] | Voltage | 0 | 0.9
40 | FALSE | FALSE | PQ_OE | 1 | 1 | FALSE | Q | 0.33 | 300 | Ideal | [5 empty] | Pctrl ref. | 0 | 0
41 | FALSE | FALSE | PQ_UE | 1 | 1 | FALSE | Q | -0.33 | 300 | Ideal | [5 empty] | Pctrl ref. | 0 | 0
42 | FALSE | TRUE | Q_control_up | 1 | 1 | FALSE | Q | 0 | 30 | Min | [5 empty] | Qctrl ref. | 0 | 0.15 |  |  | 15 | 0.33
43 | FALSE | TRUE | Q_control_down | 1 | 1 | FALSE | Q | 0.33 | 30 | Min | [5 empty] | Qctrl ref. | 0 | -0.15 |  |  | 15 | -0.33
44 | FALSE | TRUE | Qpf_ref | 1 | 1 | FALSE | PF | 1 | 30 | Min | [5 empty] | Qctrl ref. | 0 | 0.95
45 | FALSE | TRUE | Qpf_p | 1 | 1 | FALSE | PF | -0.95 | 30 | Min | [5 empty] | Pctrl ref. | 0 | 0
46 | FALSE | TRUE | Q(u)_wg | 1 | 1 | FALSE | Q(U) | 1 | 42 | Min | [5 empty] | dVoltage | 0 | 0.05 |  |  | 7 | 0 |  |  | 14 | -0.1 |  |  | 21 | 0 |  |  | 28 | 0.025 |  |  | 35 | -0.05
47 | FALSE | TRUE | Q(u)_tuning | 1 | 1 | FALSE | Q(U) | 1 | 42 | Tuning | [5 empty] | dVoltage | 0 | 0.05 |  |  | 7 | 0 |  |  | 14 | -0.1 |  |  | 21 | 0 |  |  | 28 | 0.025 |  |  | 35 | -0.05
48 | FALSE | TRUE | Q(u)_sg | 1 | 1 | FALSE | Q(U) | 1 | 42 | Max | [5 empty] | dVoltage | 0 | 0.05 |  |  | 7 | 0 |  |  | 14 | -0.1 |  |  | 21 | 0 |  |  | 28 | 0.025 |  |  | 35 | -0.05
49 | FALSE | TRUE | LVFRT_profile | 1 | 1 | FALSE | Default | 0 | 60 | Ideal | [5 empty] | Voltage | 0 | 0.15 |  |  | 0.25 | 0.15 | 0 |  | 0.25 |  | 0 |  | 0.25 |  | 0.6 |  | 1.5 |  | 0
50 | FALSE | TRUE | OVRT_profile | 1 | 1 | FALSE | Default | 0 | 70 | Ideal | [5 empty] | Voltage | 0 | 1.2 |  |  | 5 | 1.15 |  |  | 65 | 1
51 | FALSE | TRUE | Fault _rec_1 |  | 1 | FALSE | Default | 0 |  | Ideal |  |  | Fault_rec_1.csv
52 | FALSE | TRUE | Fault _rec_1_altq |  | 1 | FALSE | Q(U) | 1 |  | Ideal |  |  | Fault_rec_1.csv
53 | FALSE | TRUE | Fault _rec_2 |  | 1 | FALSE | Default | 0 |  | Ideal |  |  | Fault_rec_2.csv
54 | FALSE | TRUE | Fault _rec_2_alt |  | 1 | FALSE | Q(U) | 1 |  | Ideal |  |  | Fault_rec_2.csv
55 | FALSE | TRUE | Fault _rec_3 |  | 1 | FALSE | Default | 0 |  | Ideal |  |  | Fault_rec_3.csv
56 | FALSE | TRUE | Fault _rec_3_altq |  | 1 | FALSE | Q(U) | 1 |  | Ideal |  |  | Fault_rec_3.csv
57 | FALSE | TRUE | Fault _rec_4 |  | 1 | FALSE | Default | 0 |  | Ideal |  |  | Fault_rec_4.csv
58 | FALSE | TRUE | Fault _rec_4_altq |  | 1 | FALSE | Q(U) | 1 |  | Ideal |  |  | Fault_rec_4.csv
59 | FALSE | TRUE | Fault_3_0thres | 1 | 1 | FALSE | Default | 0 | 30 | Min | [5 empty] | 3p fault | 0 | 0 | 0
60 | FALSE | TRUE | Fault_3_25thres | 1 | 1 | FALSE | Default | 0 | 30 | Min | [5 empty] | 3p fault | 0 | 0.225 | 0.375
61 | FALSE | TRUE | Fault_3_50thres | 1 | 1 | FALSE | Default | 0 | 30 | Min | [5 empty] | 3p fault | 0 | 0.45 | 0.75
62 | FALSE | TRUE | Fault_3_75thres | 1 | 1 | FALSE | Default | 0 | 30 | Min | [5 empty] | 3p fault | 0 | 0.675 | 1.125
63 | FALSE | TRUE | Fault_3_100thres | 1 | 1 | FALSE | Default | 0 | 30 | Min | [5 empty] | 3p fault | 0 | 0.9 | 1.5
64 | FALSE | TRUE | Fault_2_0thres | 1 | 1 | FALSE | Default | 0 | 30 | Min | [5 empty] | 2p-g fault | 0 | 0 | 0
65 | FALSE | TRUE | Fault_2_25thres | 1 | 1 | FALSE | Default | 0 | 30 | Min | [5 empty] | 2p-g fault | 0 | 0.225 | 0.375
66 | FALSE | TRUE | Fault_2_50thres | 1 | 1 | FALSE | Default | 0 | 30 | Min | [5 empty] | 2p-g fault | 0 | 0.45 | 0.75
67 | FALSE | TRUE | Fault_2_75thres | 1 | 1 | FALSE | Default | 0 | 30 | Min | [5 empty] | 2p-g fault | 0 | 0.675 | 1.125
68 | FALSE | TRUE | Fault_2_100thres | 1 | 1 | FALSE | Default | 0 | 30 | Min | [5 empty] | 2p-g fault | 0 | 0.9 | 1.5
69 | FALSE | TRUE | Fault_1_0thres | 1 | 1 | FALSE | Default | 0 | 30 | Min | [5 empty] | 1p fault | 0 | 0 | 0
70 | FALSE | TRUE | Fault_1_25thres | 1 | 1 | FALSE | Default | 0 | 30 | Min | [5 empty] | 1p fault | 0 | 0.225 | 0.375
71 | FALSE | TRUE | Fault_1_50thres | 1 | 1 | FALSE | Default | 0 | 30 | Min | [5 empty] | 1p fault | 0 | 0.45 | 0.75
72 | FALSE | TRUE | Fault_1_75thres | 1 | 1 | FALSE | Default | 0 | 30 | Min | [5 empty] | 1p fault | 0 | 0.675 | 1.125
73 | FALSE | TRUE | Fault_1_100thres | 1 | 1 | FALSE | Default | 0 | 30 | Min | [5 empty] | 1p fault | 0 | 0.9 | 1.5
74 | FALSE | TRUE | Fault_3_restrike | 1 | 1 | FALSE | Default | 0 | 30 | Min | [5 empty] | 3p fault | 0 | 0.09 | 0 |  | 0.2 | 0.09 | 0 |  | 5.1 | 0.09 | 0
75 | FALSE | TRUE | Fault_1_restrike | 1 | 1 | FALSE | Default | 0 | 30 | Min | [5 empty] | 1p fault | 0 | 0 | 0 |  | 0.3 | 0 | 0
76 | FALSE | TRUE | MaxPhaseJump | 1 | 1 | FALSE | Default | 0 | 10 | Min | [5 empty] | Phase | 0 | 20 |  |  | 2.5 | 0 |  |  | 5 | -20 |  |  | 7.5 | 0
77 | FALSE | TRUE | MaxRoCoF | 1 | 0.7 | FALSE | Default | 0 | 5 | Min | [5 empty] | Frequency | 0 |  | -2 |  | 1.25 |  | 2 |  | 3.25 |  | -2 |  | 4
78 | FALSE | TRUE | Protection OV | 1 | 1 | FALSE | Default | 0 | 126.6 | Ideal | [5 empty] | Voltage | 0 | 1.099 |  |  | 61 | 1.101 |  |  | 122 | 1.149 |  |  | 123.2 | 1.151 |  |  | 124.4 | 1.199 |  |  | 125.5 | 1.201
79 | FALSE | TRUE | Protection UV | 1 | 1 | FALSE | Default | 0 | 122 | Ideal | [5 empty] | Voltage | 0 | 0.901 |  |  | 61 | 0.899
80 | FALSE | TRUE | Protection F | 1 | 1 | FALSE | Default | 0 | 5.8 | Ideal | [5 empty] | Frequency | 0 | 51.49 |  |  | 1.2 | 51.51 |  |  | 2.4 | 50 |  |  | 3.4 | 47.51 |  |  | 4.6 | 47.49
81 | FALSE | TRUE | Protection ROCOF | 1 | 1 | FALSE | Default | 0 | 5.32 | Ideal | [5 empty] | Frequency | 0 |  | 2.45 |  | 1.08 |  | 2.55 |  | 2.16 |  | 0 |  | 3.16 |  | -2.45 |  | 4.24 |  | -2.55
82 | FALSE | TRUE | Systemprotection scheme | 1 | 1 | FALSE | Default | 0 |  | Min

## datavalidation
Pctrl ref. | DK1 | Q | Max
Qctrl ref. | DK2 | PF | Min
Voltage |  | Q(U) | Tuning
dVoltage |  | Default | Ideal
Phase
Frequency
3p fault
2p-g fault
1p fault